## Sheet1
| Requirements | Implementation
|  | EnergyPlus API | Units
getters | energy consumption (power, unit Watt) | "Facility Total HVAC Electricity Demand Rate", "WHOLE BUILDING" | watts
| current room temperature | "Zone Air Temperature",zone | C
| current chiller setpoint | "Chiller Evaporator Outlet Temperature", "COOLSYS1 CHILLER 1" | C
| current boiler setpoint | "Boiler Outlet Temperature", "HEATSYS1 BOILER" | C
| current damper setpoint | "Zone Air Terminal VAV Damper Position", zone+" VAV BOX COMPONENT" | The damper position is defined as the terminal unit air mass flow rate divided by the terminal unit’s maximum air mass flow rate.
| current outdoor temperature | "Site Outdoor Air Drybulb Temperature", "Environment" | C
| target room temperature | "Zone Thermostat Air Temperature",zone | C
setters | current chiller setpoint | "System Node Setpoint","Temperature Setpoint", "COOLSYS1 SUPPLY EQUIPMENT OUTLET NODE 1" | C
| current boiler setpoint | "System Node Setpoint", "Temperature Setpoint", "HEATSYS1 SUPPLY EQUIPMENT OUTLET NODE" | C
| current damper setpoint | "System Node Setpoint", "Mass Flow Rate Setpoint", zone+" VAV BOX OUTLET NODE NAME" | The current mass flow rate setpoint at a system node in kg/s. Some controllers and equipment types sense this single setpoint.
| current outdoor temperature | "Weather Data", "Outdoor Dry Bulb", "Environment" | C